## translate it into English and k
Item No. | Item Name | Requirement No. | Requirement Text | Definition according to the Saudi Code | Suggested Repair Method | Estimated Cost (SAR)
1 | Quality of External Sockets | 2025-01-01 | In areas exposed to direct water: IP55 or higher. | External sockets must be rated IP55 or higher if exposed to water, according to SBC 401-410. | Replace the socket with an approved IP55 or higher type. | 45
1 | Quality of External Sockets | 2025-01-02 | Moisture and rust-resistant. | Rust and moisture-resistant sockets must be used in outdoor environments. | Replace the socket with a moisture and rust-resistant one. | 40
1 | Quality of External Sockets | 2025-01-03 | Grounded. | Sockets must be connected to a grounding system to discharge static electricity. | Connect the socket to the ground by a certified electrician. | 35
1 | Quality of External Sockets | 2025-01-04 | Installed at a height of no less than 30 cm from the ground. | Codes recommend installing sockets at an appropriate height to avoid direct contact with water. | Raise the socket's installation location to an appropriate height. | 30
1 | Quality of External Sockets | 2025-01-05 | Has a protective cover against weather elements. | A protective cover is required to prevent damage to internal parts from weather conditions. | Add an approved protective cover to the external socket. | 25
2 | Electrical Sockets' Load Capacity | 2025-02-01 | The socket can withstand a current of at least 13 amps. | Electrical sockets must be able to withstand a current of at least 13 amps for general use, according to SBC401-8. | Replace the socket with another one with a capacity of at least 13 amps. | 40
2 | Electrical Sockets' Load Capacity | 2025-02-02 | Connected to a source that powers its loads without exceeding the allowed limit. | The socket must be connected to an electrical source that takes load distribution into account without exceeding design limits. | Check connections and distribute loads appropriately, and do not overload the circuit. | 35
2 | Electrical Sockets' Load Capacity | 2025-02-03 | Use a wire of at least 2.5 mm² with the socket. | According to the code, the wire cross-section used with the socket must be no less than 2.5 mm² to ensure electrical safety. | Replace the wires with others with a cross-section of 2.5 mm² or more. | 30
3 | Proper Installation of Socket Wiring | 2025-03-01 | The wire ends should be insulated up to the connection point. | Full insulation of wires must be maintained up to the connection point to prevent arcing, according to SBC401-8. | Re-insulate the wire end using appropriate insulation tools and ensure its proper connection. | 20
3 | Proper Installation of Socket Wiring | 2025-03-02 | The wires must be tightly secured inside the screws. | The code stipulates that wire connections must be tight to avoid overheating or connection failure. | Reinstall the wires tightly inside the screws using an insulated screwdriver. | 25
3 | Proper Installation of Socket Wiring | 2025-03-03 | No loose or slack wires inside the socket. | There should be no looseness or disconnection in the connections to ensure safe operation. | Check all connections, ensure they are tight and not slack, and replace the socket if necessary. | 25
4 | Coverage of External Electrical Sockets | 2025-04-01 | Has a weather-resistant cover (IP55 or higher). | The code requires using a cover for external sockets with a protection standard of at least IP55 to resist water and dust (SBC401-8). | Replace the cover with a new one that has an IP55 or higher protection rating. | 45
4 | Coverage of External Electrical Sockets | 2025-04-02 | The cover is free of cracks or breaks. | The code stipulates that the cover must be intact and free of breaks that affect insulation. | Replace the cracked or broken cover with a new, weather-resistant one. | 35
4 | Coverage of External Electrical Sockets | 2025-04-03 | The cover is tightly secured without gaps. | The cover must be securely fastened to prevent the entry of dust or water. | Re-secure the cover using appropriate fasteners to ensure a tight seal. | 25
5 | Quality of Finish Around Electrical Sockets | 2025-05-01 | The plaster or tiles around the socket are not cracked or chipped. | The Saudi code mandates maintaining the integrity of finishes around electrical installations to prevent cracks that could damage insulation or lead to moisture (SBC401). | Repair the plaster or replace the cracked or chipped tiles using compatible materials. | 40
5 | Quality of Finish Around Electrical Sockets | 2025-05-02 | The socket is aligned with the wall level without a clear tilt. | Electrical devices must be installed level with the wall for aesthetic and safety reasons. | Reinstall the socket and adjust its level using a spirit level. | 30
5 | Quality of Finish Around Electrical Sockets | 2025-05-03 | No gaps or cracks in the vicinity of the socket. | Sockets must be installed without gaps that affect their fastening or insulation. | Fill gaps with a moisture-resistant material and re-finish the area around the socket. | 25
6 | Horizontal Alignment of Electrical Sockets | 2025-06-01 | Adjust the socket's installation angle with a spirit level. | The code requires that electrical devices be installed accurately and achieve horizontal alignment to ensure performance and visual safety. | Undo the socket and adjust its angle using a spirit level before final fastening. | 30
6 | Horizontal Alignment of Electrical Sockets | 2025-06-02 | The socket tilt should not exceed ±2 degrees. | The socket's tilt should not exceed ±2 degrees to maintain the balance of connections and safe use. | Precisely adjust the socket in its place and prevent any tilt using accurate measuring tools. | 20
6 | Horizontal Alignment of Electrical Sockets | 2025-06-03 | Fasten the socket on the same horizontal line with the adjacent sockets. | All sockets must be at the same level to achieve symmetry and prevent malfunctions resulting from tension or bending. | Fasten all sockets on a single level using a laser or a horizontal level with a mounting template. | 25
7 | Safety of Visible or External Wiring | 2025-07-01 | Securely fasten wiring on walls or ceilings. | External wiring must be well-secured to prevent vibration or disconnection, according to code requirements (SBC401). | Re-fasten the wiring using appropriate clips or clamps. | 30
7 | Safety of Visible or External Wiring | 2025-07-02 | No cracks or damage in the protective conduits. | Protective conduits must be intact and free of any damage that threatens electrical insulation or connection. | Replace damaged conduits with new ones that comply with specifications. | 45
7 | Safety of Visible or External Wiring | 2025-07-03 | Confirm the use of conduits made of approved, heat- and moisture-resistant materials. | The materials used in the wiring must comply with the specifications approved by the Saudi Standards, Metrology and Quality Organization. | Ensure the quality of the materials and use heat- and moisture-resistant conduits after checking approved brands. | 60
8 | Powering Electrical Loads According to the Plan | 2025-08-01 | Confirm that all electrical points are powered from the correct circuits according to the approved plan. | The Saudi code requires load distribution according to the approved executive plans to achieve operational efficiency and safety. | Review the plan and ensure that the actual circuits match it, and reconnect any incorrect circuit. | 80
8 | Powering Electrical Loads According to the Plan | 2025-08-02 | Confirm the presence of a sub-distribution board when needed, as shown in the plan. | In large or multi-use projects, the presence of sub-boards is required to reduce the load on the main board. | Add a sub-distribution board if one is not present and connect it correctly to the main board. | 250
8 | Powering Electrical Loads According to the Plan | 2025-08-03 | Confirm that loads are evenly distributed among the phases to prevent overloading. | Distributing loads among the phases is essential to prevent fluctuations and frequent tripping, and it is one of the standards for the quality of electrical execution. | Measure loads and redistribute them to ensure balance between the phases using a load measuring device. | 100
9 | Separation of Lighting Circuits from Sockets | 2025-09-01 | Confirm the presence of separate circuit breakers for both lighting and sockets. | The SBC401 code requires separating lighting circuits from power circuits to ensure safety and ease of maintenance. | Add separate circuit breakers or redistribute circuits to ensure separation. | 70
9 | Separation of Lighting Circuits from Sockets | 2025-09-02 | Confirm that sockets and lighting are not powered from the same circuit breaker. | Preventing power overlap reduces the risk of overloading and ensures proper power distribution. | Separate lighting lines from socket lines and reconnect them to the appropriate circuit breakers. | 150
9 | Separation of Lighting Circuits from Sockets | 2025-09-03 | Confirm that the separation is shown in the electrical plan. | Documenting this separation in the electrical plan is a requirement to ensure compliant execution. | Modify or update the electrical plan to reflect the new changes. | 100
10 | Suitability of Wire Cross-section for the Electrical Load | 2025-10-01 | Confirm that the wire cross-section is not less than 2.5 mm² for sockets. | The code requires using wire cross-sections that are suitable for the current they carry to prevent overheating and fire. | Replace wires with an unsuitable cross-section with a 2.5 mm² wire for sockets. | 180
10 | Suitability of Wire Cross-section for the Electrical Load | 2025-10-02 | Confirm the use of a 1.5 mm² wire for lighting only, if there are no high loads. | It is permissible to use a 1.5 mm² wire for lighting provided there are no loads that exceed its capacity. | Re-check the lighting circuits and replace the wire if the allowed load is exceeded. | 120
10 | Suitability of Wire Cross-section for the Electrical Load | 2025-10-03 | Confirm that there are no wirings with wires less than the recommended size. | The presence of wiring with thin wires exposes the system to danger and is a clear violation. | Remove non-compliant wires and replace them according to the required specifications. | 200
11 | Grounding Connection | 2025-11-01 | Confirm the presence of a grounding wire connected to every electrical circuit. | The SBC401 code requires an effective grounding connection in all circuits to provide protection from electric shocks. | Install a new grounding wire and connect it to the distribution board and the grounding rod. | 150
11 | Grounding Connection | 2025-11-02 | Confirm the use of an appropriate cross-section for the grounding wire, not less than 2.5 mm². | The wire used for grounding must have an appropriate cross-section to safely connect the current in case of a malfunction. | Replace the grounding wire if the cross-section does not comply with specifications. | 100
11 | Grounding Connection | 2025-11-03 | Confirm that the grounding resistance does not exceed 5 ohms according to SBC401. | The acceptable grounding resistance must not exceed 5 ohms to achieve effective performance. | Check the grounding system and update it by adding additional rods or improving the quality of the connection. | 180
12 | Load Distribution on Circuit Breakers | 2025-12-01 | Confirm that each group of loads is linked to a dedicated circuit breaker. | The code requires distributing loads on separate circuit breakers to avoid overloading and the risk of melting. | Redistribute loads on separate circuit breakers according to the power drawn. | 170
12 | Load Distribution on Circuit Breakers | 2025-12-02 | Confirm that the circuit breakers are distributed to reduce excessive loads. | The code requires designing the network in a way that minimizes the possibility of service interruption due to overloading. | Add new circuit breakers or modify the locations of loads to reduce the load on a single circuit breaker. | 160
12 | Load Distribution on Circuit Breakers | 2025-12-03 | Confirm a balance between the three-phase and sub-circuit breakers in the electrical panel. | It must be ensured that the panels contain a balanced distribution that maintains the efficiency of the electrical system. | Review the load distribution in the panel and organize it according to the recommended electrical balance. | 180
13 | Identification of Electrical Circuits | 13.1 | Confirm the presence of identification labels on all circuit breakers in the distribution panel. | The SBC401 code requires identifying electrical circuits to facilitate maintenance and reduce operational errors. | Add identification labels for each circuit breaker using moisture- and heat-resistant materials. | 60
13 | Identification of Electrical Circuits | 13.2 | Confirm that the names of the rooms or loads associated with each circuit breaker are written. | The source of each circuit breaker must be clarified with a phrase or symbol that indicates the location or type of load associated with it. | Update and clarify the names of loads or rooms associated with each circuit breaker. | 50
13 | Identification of Electrical Circuits | 13.3 | Confirm that the labels are clear and not easily damaged or removed. | The code requires that labels be permanent, clear, and well-secured on the panel. | Secure labels permanently using strong adhesives or thermal printing techniques. | 40
14 | Overload Protection | 14.1 | Confirm the presence of appropriate protection circuit breakers for each electrical circuit. | The Saudi code requires the installation of protection circuit breakers to prevent the risks of overloading and fires. | Replace the current circuit breaker with another that is compatible with the rated load. | 150
14 | Overload Protection | 14.2 | Confirm that the circuit breakers are compatible with the allowed load current. | The circuit breaker must be appropriate in terms of capacity and current to prevent exceeding the maximum limit. | Review the load currents and modify unsuitable circuit breakers. | 130
14 | Overload Protection | 14.3 | Confirm the absence of signs of burning or overheating resulting from overloading. | The code prohibits any signs of thermal damage that indicate overloading or poor design. | Isolate the damaged line and achieve a proper load distribution to prevent overheating. | 120
15 | Lighting Distribution | 15.1 | Confirm the presence of sufficient lighting points to cover all areas. | The code requires providing sufficient and safe lighting in all used areas. | Add new lighting points to cover unlit areas. | 180
15 | Lighting Distribution | 15.2 | Confirm the presence of lighting control switches in easily accessible locations. | Switches must be installed at an appropriate height and in locations that are easy to use. | Move or add control switches to strategic locations. | 100
15 | Lighting Distribution | 15.3 | Confirm the distribution of lighting is balanced to avoid shadows or glare. | The code recommends distributing lighting points in a balanced way to provide visual comfort and efficiency. | Adjust the locations of the lamps or use appropriate lighting units for better distribution. | 120
16 | Height of Electrical Sockets | 16.1 | Confirm the installation of sockets at a height of no less than 30 cm from the floor level. | The code requires installing sockets at a safe height from the floor level to ensure safety. | Reinstall the socket at a height that complies with specifications. | 90
16 | Height of Electrical Sockets | 16.2 | Confirm that sockets in wet areas are at a height of no less than 110 cm. | In areas exposed to moisture, the code specifies a higher height to avoid water exposure. | Raise the socket in wet areas to the height recommended by the code. | 120
16 | Height of Electrical Sockets | 16.3 | Confirm the standardization of socket height within the same room for finishing consistency. | The code stipulates the consistency of socket distribution to facilitate use and achieve visual quality. | Adjust the height of inconsistent sockets in the same room. | 100
17 | Consistency of Socket Distribution | 17.1 | Confirm that sockets are distributed in a balanced way within the spaces. | The code emphasizes the balanced distribution of sockets to avoid random wiring. | Add or move sockets to distribute them evenly in the space. | 140
17 | Consistency of Socket Distribution | 17.2 | Confirm the distribution of sockets next to every expected point of use (desk, bed, kitchen). | The code requires the presence of a socket at every point where use is expected. | Add sockets in underserved areas according to expected use. | 120
17 | Consistency of Socket Distribution | 17.3 | Confirm the presence of a sufficient number of sockets that covers the need without wire congestion. | The code requires a minimum number of sockets in each room based on the area and use. | Add sockets or extend new points to reduce the use of external connectors. | 150
18 | Distribution of Electrical Switches | 18.1 | Confirm the placement of switches near the entrances of rooms. | The code stipulates installing switches at the entrances of rooms for easy access upon entry. | Move the switch to its correct location at the entrance. | 80
18 | Distribution of Electrical Switches | 18.2 | Confirm the installation of switches at a uniform height of about 120 cm from the ground. | The code indicates standardizing the height of switches for safety and aesthetic purposes. | Re-adjust the height of switches to be on a single level. | 90
18 | Distribution of Electrical Switches | 18.3 | Confirm that the distribution of switches is compatible with the distribution of lighting units. | The code requires the compatibility of switch distribution with lighting to reduce wiring chaos. | Modify the electrical circuits to fit the new distribution. | 110
19 | Safety of Electrical Wiring | 19.1 | Confirm that electrical wiring is inside plastic or metal conduits. | The code requires that wiring be inside conduits to protect it from damage and friction. | Re-wire the cables inside approved and fastened conduits. | 150
19 | Safety of Electrical Wiring | 19.2 | Confirm the absence of sharp tears or bends in the wiring. | The code stipulates that wiring must be executed in a straight and safe manner without folds that affect the wire. | Replace or rearrange wires in a safe and straight manner. | 100
19 | Safety of Electrical Wiring | 19.3 | Confirm that wiring is away from heat and moisture sources. | The code indicates preventing wiring next to heat sources to avoid fire risks. | Move wiring away from heat sources or insulate it well. | 130
20 | Distance Between Light Switches and Doors | 20.1 | Confirm that the distance between the switch and the edge of the door is not less than 15 cm. | The code requires a sufficient distance between switches and doors to avoid obstacles. | Move the switch to a safe distance from the door, not less than 15 cm. | 70
20 | Distance Between Light Switches and Doors | 20.2 | Confirm that the switch is easily accessible when the door is opened. | The switch should be within reach without having to go behind the door. | Install the switch in a suitable position that is easy to access. | 65
20 | Distance Between Light Switches and Doors | 20.3 | Confirm that the switch's location does not obstruct the installation of wall accessories. | The code requires that the location of switches does not conflict with the design of rooms and wall accessories. | Redistribute switches so they do not conflict with daily use. | 75
21 | Organization of Light Switches According to Use | 21.1 | Confirm that each switch controls one specific light circuit. | The code emphasizes the importance of clear switch distribution and dedicating each switch to a specific function. | Reconnect the circuits so that each switch is dedicated to a single circuit. | 85
21 | Organization of Light Switches According to Use | 21.2 | Confirm the presence of labels or symbols that explain the function of each switch. | The code encourages the use of distinctive labels to facilitate use and reduce errors. | Install labels or signs on switches that explain their use. | 30
21 | Organization of Light Switches According to Use | 21.3 | Confirm that the lighting circuits do not overlap with each other. | The code prevents random connections between circuits to avoid malfunctions and electrical interference. | Separate overlapping connections and organize the distribution of electrical loads. | 90
22 | Safety of Electrical Switches from Damage | 22.1 | Confirm that the switches are free of cracks, breaks, or visible damage. | The code emphasizes the need for the safety of the cover and the external structure of the switch to maintain safety. | Replace cracked or broken switches with new, approved ones. | 30
22 | Safety of Electrical Switches from Damage | 22.2 | Confirm that the switches operate smoothly without interruption or sticking. | The code emphasizes the importance of smooth operation of switches to avoid electrical malfunctions. | Inspect the switch and replace it if there is an internal mechanical defect. | 40
22 | Safety of Electrical Switches from Damage | 22.3 | Confirm the absence of excessive heat in the switch body during operation. | The code indicates that excessive heat in switches may indicate an overload or internal defect. | Measure the temperature and replace the switch or reduce the load if necessary. | 60
23 | Secure Installation of Switches | 23.1 | Confirm the switches are securely fastened to walls or panels without shaking or movement. | The code emphasizes that all electrical installations must be securely fastened to prevent accidents. | Reinstall the switch using a suitable mounting base. | 40
23 | Secure Installation of Switches | 23.2 | Confirm the absence of a gap between the switch and the wall surface. | The code stipulates the need for secure fastening to prevent the entry of dust or moisture. | Treat the wall surface or replace the mounting box to ensure complete contact. | 35
23 | Secure Installation of Switches | 23.3 | Confirm the use of original and appropriate screws or fastening tools. | The code requires the use of fastening tools recommended by the manufacturer to prevent malfunctions. | Use compliant screws and replace old, damaged ones. | 25
24 | Height of Switches from Floor Level | 24.1 | Confirm that the height of switches is not less than 110 cm from the floor. | The code stipulates that switches must be installed at a height that ensures safety and ease of access. | Reinstall the switches at an appropriate height using a new mounting base. | 50
24 | Height of Switches from Floor Level | 24.2 | Confirm the standardization of height for all switches within the same area. | The code requires consistency in height within the same space to achieve aesthetics and functionality. | Adjust the locations of inconsistent switches to standardize their height. | 40
24 | Height of Switches from Floor Level | 24.3 | Confirm that the height is compatible with the requirements of people with disabilities in designated areas. | The code indicates the need to comply with universal access considerations in public and service locations. | Adhere to the specifications of the universal access code and re-install if needed. | 60
25 | Distribution of Switches Inside Rooms | 25.1 | Confirm the presence of a switch at every room entrance. | The code requires the presence of light switches at room entrances to facilitate safe operation. | Add a new switch at the entrance with appropriate wiring. | 60
25 | Distribution of Switches Inside Rooms | 25.2 | Confirm that switches are distributed to serve lighting and appliances practically. | The code stipulates the distribution of switches to achieve effective use of the spaces. | Modify the locations of switches or add new ones as needed. | 70
25 | Distribution of Switches Inside Rooms | 25.3 | Confirm that switches are not behind fully opened doors. | The code indicates the need to ensure easy access to switches and that they are not blocked by doors. | Move switches from behind doors to exposed and easily accessible locations. | 50
26 | Quality of Switch Cover Installation | 26.1 | Confirm that the cover is securely fastened and does not move when touched. | The code requires covers to be securely installed for protection and to prevent the entry of dust or moisture. | Re-fasten the cover using original screws or replace it. | 30
26 | Quality of Switch Cover Installation | 26.2 | Confirm that the cover is free of any obvious cracks or damage. | The code stipulates the safety of external components to avoid electrical hazards. | Replace the damaged cover with a new one of the same specifications. | 25
26 | Quality of Switch Cover Installation | 26.3 | Confirm that the color of the cover matches the rest of the switches and sockets. | The code indicates the importance of aesthetic coordination as part of the quality of final finishes. | Replace the cover with a color that matches the rest of the switches or install a new set. | 40
27 | Harmony of Switches with Wall Design | 27.1 | Confirm that the location of the switches does not distort the overall appearance of the space. | The code stipulates aesthetic considerations and the appropriate location of switches to ensure comfort and ease of access. | Move switches to locations that are more consistent with the wall design. | 60
27 | Harmony of Switches with Wall Design | 27.2 | Confirm the installation of switches at a level consistent with the rest of the architectural elements. | The code requires the compatibility of switch height and locations with safe and comfortable use. | Re-adjust the height and location using new boxes. | 70
27 | Harmony of Switches with Wall Design | 27.3 | Confirm that the switches do not obstruct the use of spaces (e.g., behind curtains or furniture). | The code emphasizes that switches should not obstruct user movement or be used behind moving elements. | Move switches away from obstacles to ensure easy access. | 65
28 | Switches Matching Electrical Plans | 28.1 | Confirm that the locations of switches match the approved electrical plans. | The code requires strict adherence to the locations and distribution of switches as stated in the approved plans. | Compare the actual locations with the plan and reinstall the switches if necessary. | 55
28 | Switches Matching Electrical Plans | 28.2 | Confirm that the number of switches matches what is shown in the plan. | The code emphasizes the importance of verifying that the number of switches meets functional and design requirements. | Add or remove switches to match the required number. | 60
28 | Switches Matching Electrical Plans | 28.3 | Confirm the function of each switch as specified in the plan (e.g., lighting, fan, etc.). | The code stipulates that the function of the switch must match the purpose specified in the design to avoid misuse. | Correct the switch connections to perform the functions specified in the plan. | 65
29 | Safety of Control Switches | 29.1 | Confirm that the switches are free of any cracks or visible damage. | The code requires that switches be mechanically sound and free of defects to ensure safety. | Replace any damaged or cracked switch. | 50
29 | Safety of Control Switches | 29.2 | Confirm that the switches operate normally without sticking or difficulty. | The code stipulates the need for smooth operation of switches to ensure safe use for users. | Repair or replace a switch that sticks or does not work smoothly. | 60
29 | Safety of Control Switches | 29.3 | Confirm that the cover is securely fastened and does not move during use. | The code requires securely fastening the switch cover to protect against accidental contact or damage. | Re-fasten the cover or replace it if it is not secure. | 40
30 | Switch Covers Matching Specifications | 30.1 | Confirm that the cover is made of flame-resistant material. | The code requires the use of flame-resistant materials in switch components to ensure safety. | Replace the cover with an approved cover made of flame-resistant material. | 45
30 | Switch Covers Matching Specifications | 30.2 | Confirm the absence of cracks or gaps in the cover. | The code stipulates that covers must be intact and free of any cracks that affect performance or safety. | Install a new, intact, and cohesive cover. | 40
30 | Switch Covers Matching Specifications | 30.3 | Confirm that the color of the cover is consistent with the rest of the room's components. | The code recommends considering aesthetic aspects and visual integration in electrical finishes. | Replace the cover with a consistent color according to interior design requirements. | 30
31 | Level of Sockets from the Floor | 31.1 | Confirm that the socket's height from the floor is not less than 30 cm. | The code requires a safe height for sockets to reduce the risk of electrical contact and potential damage. | Reinstall the socket in a higher location to ensure the allowed height. | 70
31 | Level of Sockets from the Floor | 31.2 | Confirm the standardization of height for all sockets in the same room. | The code stipulates aesthetic and functional standardization of socket locations in interior spaces. | Adjust the locations of inconsistent sockets to standardize the height. | 50
31 | Level of Sockets from the Floor | 31.3 | Confirm that the height is measured using accurate tools (laser meter or level). | The code requires the adoption of accurate measuring tools to ensure compliance with specifications. | Use accurate measuring tools to adjust the installation level during work. | 20
32 | Locations of Electrical Switches | 32.1 | Confirm the presence of switches next to doors and at an appropriate height. | The code recommends installing switches in easily accessible locations, usually at room entrances and at a height of approximately 110-120 cm. | Reinstall switches in a suitable location near the door and at an approved height. | 60
32 | Locations of Electrical Switches | 32.2 | Confirm that the locations of switches allow for easy access without obstacles. | The code requires that switches be in locations that are easy to use without having to pass obstacles. | Move switches to a more easily accessible location according to standards. | 50
32 | Locations of Electrical Switches | 32.3 | Confirm that switches are a safe distance from water sources. | The code stipulates keeping switches away from damp areas such as basins and sinks. | Move switches away from water areas and install them in a safe location. | 55
33 | Distribution of Electrical Loads | 33.1 | Confirm the distribution of loads evenly among the circuit breakers. | The code requires distributing electrical loads evenly to prevent overheating in wires and circuit breakers. | Redistribute loads among circuit breakers with a study of the load for each circuit. | 120
33 | Distribution of Electrical Loads | 33.2 | Confirm the absence of circuits crowded with high electrical loads. | The code warns against grouping large loads on the same circuit to avoid the risk of melting or fire. | Divide circuits that contain more than one high-consumption device. | 100
33 | Distribution of Electrical Loads | 33.3 | Confirm the presence of separate circuits for high-consumption electrical appliances. | The code recommends separating high-consumption appliances such as air conditioners and water heaters with separate circuits to ensure protection. | Add separate circuit breakers for large appliances and connect them to a separate circuit. | 150
34 | Electrical Grounding System | 34.1 | Confirm the presence of a grounding system connected to all electrical circuits. | The code requires a complete grounding system to discharge excess currents and prevent electric shocks. | Install a grounding rod and connect it to the grounding distribution box according to the code. | 300
34 | Electrical Grounding System | 34.2 | Confirm the measurement of grounding resistance and that it is within the allowed limit (less than 5 ohms). | The code specifies a maximum grounding resistance of 5 ohms to ensure effectiveness. | Re-measure the grounding resistance using a specialized device and ensure its compliance. | 150
34 | Electrical Grounding System | 34.3 | Confirm the safety of grounding wire connections and the absence of disconnection or corrosion. | The code requires periodic inspection of grounding connections and that they are well-fastened to avoid damage or interruption. | Inspect the cables, replace damaged ones, and tighten the connections to the metal points. | 120